Fire Safety Maintenance Checklist – Non-residential Premises

| Check frequency and type | Y | N | N/ A | Who / Responsibility | Comment |
| --- | --- | --- | --- | --- | --- |
| Daily checks (not normally recorded) |  |  |  |  |  |
| Escape routes |  |  |  |  |  |
| Can all fire exits be opened immediately and easily? | ☐ | ☐ | ☐ |  |  |
| Are fire doors clear of obstructions? | ☐ | ☐ | ☐ |  |  |
| Are escape routes clear? | ☐ | ☐ | ☐ |  |  |
| Fire warning systems |  |  |  |  |  |
| Is the indicator panel showing ‘normal’? | ☐ | ☐ | ☐ |  |  |
| Are whistles, gongs or air horns in place? | ☐ | ☐ | ☐ |  |  |
| Escape lighting |  |  |  |  |  |
| Are luminaires and exit signs in good condition and undamaged? | ☐ | ☐ | ☐ |  |  |
| Is emergency lighting and sign lighting working correctly? | ☐ | ☐ | ☐ |  |  |
| Firefighting equipment |  |  |  |  |  |
| Are all fire extinguishers in place? | ☐ | ☐ | ☐ |  |  |
| Are fire extinguishers clearly visible? | ☐ | ☐ | ☐ |  |  |
| Are vehicles blocking fire hydrants or access to them? | ☐ | ☐ | ☐ |  |  |
| Weekly checks |  |  |  |  |  |
| Escape routes |  |  |  |  |  |
| Do all emergency fastening devices to fire exits (push bars and pads, etc.) work correctly? | ☐ | ☐ | ☐ |  |  |
| Are external routes clear and safe? | ☐ | ☐ | ☐ |  |  |
| Fire warning systems |  |  |  |  |  |
| Does testing a manual call point send a signal to the indicator panel? (Disconnect the link to the receiving centre or tell them you are doing a test.) | ☐ | ☐ | ☐ |  |  |
| Did the alarm system work correctly when tested? | ☐ | ☐ | ☐ |  |  |
| Did staff and other people hear the fire alarm? | ☐ | ☐ | ☐ |  |  |
| Did any linked fire protection systems operate correctly? (e.g. magnetic door holder released, smoke curtains drop) | ☐ | ☐ | ☐ |  |  |
| Do all visual alarms and/or vibrating alarms and pagers (as applicable) work? | ☐ | ☐ | ☐ |  |  |
| Do voice alarm systems work correctly? Was the message understood? | ☐ | ☐ | ☐ |  |  |
| Escape lighting |  |  |  |  |  |
| Are charging indicators (if fitted) visible? | ☐ | ☐ | ☐ |  |  |
| Firefighting equipment |  |  |  |  |  |
| Is all equipment in good condition? | ☐ | ☐ | ☐ |  |  |
| Additional items from manufacturer’s recommendations (specialist equipment etc.). | ☐ | ☐ | ☐ |  |  |
| Monthly checks |  |  |  |  |  |
| Escape routes |  |  |  |  |  |
| Do all electronic release mechanisms on escape doors work correctly? Do they ‘fail safe’ in the open position? | ☐ | ☐ | ☐ |  |  |
| Do all automatic opening doors on escape routes ‘fail safe’ in the open position? | ☐ | ☐ | ☐ |  |  |
| Are fire door seals and self-closing devices in good condition? | ☐ | ☐ | ☐ |  |  |
| Do all roller shutters provided for fire compartmentation work correctly? | ☐ | ☐ | ☐ |  |  |
| Are external escape stairs safe? | ☐ | ☐ | ☐ |  |  |
| Do all internal self-closing fire doors work correctly? | ☐ | ☐ | ☐ |  |  |
| Escape lighting |  |  |  |  |  |
| Do all luminaires (emergency lights) and exit signs function correctly when tested? | ☐ | ☐ | ☐ |  |  |
| Have all emergency generators been tested? (Normally run for one hour.) | ☐ | ☐ | ☐ |  |  |
| Firefighting equipment |  |  |  |  |  |
| Is the pressure in ‘stored pressure’ fire extinguishers correct? | ☐ | ☐ | ☐ |  |  |
| Additional items from manufacturer’s recommendations (specialist equipment etc.). | ☐ | ☐ | ☐ |  |  |
| Three-monthly checks |  |  |  |  |  |
| General |  |  |  |  |  |
| Are any emergency water tanks/ponds at their normal capacity? | ☐ | ☐ | ☐ |  |  |
| Are vehicles blocking fire hydrants or access to them? | ☐ | ☐ | ☐ |  |  |
| Additional items from manufacturer’s recommendations (specialist equipment etc.). | ☐ | ☐ | ☐ |  |  |
| Six-monthly checks |  |  |  |  |  |
| General |  |  |  |  |  |
| Has any firefighting or emergency evacuation (eg. disabled evacuation) lift been tested by a competent person? | ☐ | ☐ | ☐ |  |  |
| Has any sprinkler system been tested by a competent person? | ☐ | ☐ | ☐ |  |  |
| Have the release and closing mechanisms of any fire-resisting compartment doors and shutters been tested by a competent person? | ☐ | ☐ | ☐ |  |  |
| Fire warning system |  |  |  |  |  |
| Has the system been checked by a competent person? | ☐ | ☐ | ☐ |  |  |
| Escape lighting |  |  |  |  |  |
| Additional items from manufacturer’s recommendations (specialist equipment etc.). | ☐ | ☐ | ☐ |  |  |
| Annual checks |  |  |  |  |  |
| Escape routes |  |  |  |  |  |
| Do all self-closing fire doors fit correctly? | ☐ | ☐ | ☐ |  |  |
| Is escape route compartmentation in good repair? | ☐ | ☐ | ☐ |  |  |
| Escape lighting |  |  |  |  |  |
| Do all luminaires operate on test for their full rated duration? | ☐ | ☐ | ☐ |  |  |
| Has the system been checked by a competent person? | ☐ | ☐ | ☐ |  |  |
| Firefighting equipment |  |  |  |  |  |
| Has all firefighting equipment been checked by a competent person? | ☐ | ☐ | ☐ |  |  |
| Miscellaneous |  |  |  |  |  |
| Has any dry/wet rising fire main been tested by a competent person? | ☐ | ☐ | ☐ |  |  |
| Has the smoke and heat ventilation system been tested by a competent person? | ☐ | ☐ | ☐ |  |  |
| Has external access for the fire service been checked for ongoing availability? | ☐ | ☐ | ☐ |  |  |
| Have any firefighters’ switches been tested? | ☐ | ☐ | ☐ |  |  |
| Has the fire hydrant bypass flow valve control been tested by a competent person? | ☐ | ☐ | ☐ |  |  |
| Are any necessary fire service direction signs in place? | ☐ | ☐ | ☐ |  |  |
| Periodic |  |  |  |  |  |
| Is the premises electrical installation inspected in accordance with the IET Wiring Regulations/BS 7671- at least every 5 years? | ☐ | ☐ | ☐ |  |  |
| Have all actions raised in the premises electrical installation report (above) been actioned and closed out? | ☐ | ☐ | ☐ |  |  |
| Has portable electrical equipment been PAT tested at least every 12 months, 24 months or 48 months as determined by the location risk (see intranet) https://staff.shropshire.gov.uk/policies-and-guidance/health-and-safety/registration-inspection-and-testing-of-portable-and-transportable-electrical-equipment/ )? And for high risk locations: - 3 monthly on construction sites? - 6 monthly in industrial site and commercial kitchen? | ☐ | ☐ | ☐ |  |  |